{"text_format":"1","workbook":"xlsx","n_sheets":4,"sheets":["Cover Sheet"," Mandatory - DC AC Motorized","put in vendor schedule","Technical Requirements1"],"not_rendered":{"charts":0,"images":1,"macros":0,"external_links":0,"defined_names":6,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Cover Sheet","index":0,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":" Mandatory - DC AC Motorized","index":1,"n_rows":56,"n_cols":19,"rows_kept":56,"cut":false,"hidden":false,"merged":[[18,1,18,18],[14,1,14,18],[8,1,8,18],[29,1,31,1],[29,3,31,3],[27,3,28,3],[29,0,31,0],[22,0,23,0],[22,1,23,1],[27,0,28,0],[27,1,28,1],[6,4,6,10],[51,1,51,2],[52,1,52,2],[53,1,53,2],[34,7,35,7],[9,1,9,2],[10,1,10,2],[11,1,11,2],[12,1,12,2],[13,1,13,2],[15,1,15,2],[16,1,16,2],[17,1,17,2],[19,1,19,2],[20,1,20,2],[22,3,23,3],[54,1,54,2],[32,0,35,0],[36,0,39,0],[46,1,46,2],[47,1,47,2],[48,1,48,2],[49,1,49,2],[50,1,50,2],[40,1,40,2],[41,1,41,2],[42,1,42,2],[43,1,43,2],[44,1,44,2],[45,1,45,18],[34,17,35,17],[34,12,35,12],[34,13,35,13],[34,14,35,14],[34,15,35,15],[34,16,35,16],[36,3,39,3],[34,4,35,4],[34,5,35,5],[32,3,35,3],[34,6,35,6],[55,1,55,2],[6,12,6,18],[13,3,13,18],[17,3,17,18],[25,1,25,2],[26,1,26,2],[21,1,21,2],[34,10,35,10],[24,1,24,2],[34,18,35,18],[34,8,35,8],[34,9,35,9],[34,2,35,2],[34,11,35,11],[32,1,35,1],[36,1,39,1]]}
["TECHNICAL SCHEDULES"]
["MANDATORY REQUIREMENTS"]
["All the Equipments described in this Schedule shall comply with the Mandatory Technical Requirements listed below."]
["TECHNICAL SCHEDULES"]
["AM-P0000-24 - DISCONNECTORS AND EARTH SWITCHES 362KV"]
[]
[null,null,null,null,"MANDATORY REQUIREMENTS FOR MANUAL AND MOTORIZED (MOTORS WITH DC SUPPLY ) DISCONNECTORS & EARTHSWITCHES (ITEM 1A TO ITEM 3)",null,null,null,null,null,null,null,"MANDATORY REQUIREMENTS FOR MOTORIZED (MOTORS WITH AC SUPPLY) DISCONNECTORS & EARTHSWITCHES (ITEM 5A TO ITEM 7)"]
["No","Description",null,"Unit","Item 1A","Item 1B","Item 1C","Item 2A","Item 2B","Item 2C","Item 3","Item 4","Item 5A","Item 5B","Item 5C","Item 6A","Item 6B","Item 6C","Item 7"]
[1,"Particulars of System"]
[1.1000000000000001,"System Highest Voltage",null,"kV",362,362,362,362,362,362,362,362,362,362,362,362,362,362,362]
[1.2,"Nominal Voltage",null,"kV",330,330,330,330,330,330,330,330,330,330,330,330,330,330,330]
[1.3,"Phases",null,"Nos",3,3,3,3,3,3,3,3,3,3,3,3,3,3,3]
[1.4,"Rated Frequency",null,"Hz",50,50,50,50,50,50,50,50,50,50,50,50,50,50,50]
[1.5,"System neutral earthing conditions",null,"Effectively Earthed"]
[2,"Service Conditions"]
[2.1,"Minimun ambient temperature",null,"Celcius",-5,-5,-5,-5,-5,-5,-5,-5,-5,-5,-5,-5,-5,-5,-5]
[2.2000000000000002,"Maximum ambient temperature",null,"Celcius",45,45,45,45,45,45,45,45,45,45,45,45,45,45,45]
[2.2999999999999998,"Corrosion level (AS/NZS 2312:1 & AS/NZS 2312:2)",null,"C5 - M: Very High (Marine)"]
[3,"Characteristics of a Disconnector or Earth Swith"]
[3.1,"Number of poles",null,"Nos",3,3,3,3,3,3,3,3,3,3,3,3,3,3,3]
[3.2,"Installation Type",null,null,"Outdoor","Outdoor","Outdoor","Outdoor","Outdoor","Outdoor","Outdoor","Outdoor","Outdoor","Outdoor","Outdoor","Outdoor","Outdoor","Outdoor","Outdoor"]
[3.3,"Insulation medium",null,null,"Air","Air","Air","Air","Air","Air","Air","Air","Air","Air","Air","Air","Air","Air","Air"]
[3.4,"Rated Power Frequency Withstand Voltage (RMS Value)","Phase-to-earth and Between Phases","kV rms",450,450,450,450,450,450,450,"N/A",450,450,450,450,450,450,450]
[null,null,"Across Open Switching Device and/or Isolating Distance",null,520,520,520,520,520,520,520,"N/A",520,520,520,520,520,520,520]
[3.5,"Disconnector Rated curent",null,"A rms",4000,4000,4000,4000,4000,4000,"N/A","N/A",4000,4000,4000,4000,4000,4000,"N/A"]
[3.6,"Maximum Prospective Short Circuit Current",null,"kA rms",50,50,50,50,50,50,50,"N/A",50,50,50,50,50,50,50]
[3.7,"Duration of Short Circuit",null,"s",1,1,1,1,1,1,1,"N/A",1,1,1,1,1,1,1]
[3.8,"Rated Lightning Impulse Withstand Voltage ","Phase-to-earth and Between Phases","kV peak",1175,1175,1175,1175,1175,1175,1175,"N/A",1175,1175,1175,1175,1175,1175,1175]
[null,null,"Across Open Switching Device and/or Isolating Distance",null,"1175(+205)","1175(+205)","1175(+205)","1175(+205)","1175(+205)","1175(+205)","1175(+205)","N/A","1175(+205)","1175(+205)","1175(+205)","1175(+205)","1175(+205)","1175(+205)","1175(+205)"]
[3.9,"Rated Switching Impulse Withstand Voltage","Phase-to-earth and Across Open Switching Device","kV peak",950,950,950,950,950,950,950,"N/A",950,950,950,950,950,950,950]
[null,null,"Between Phases",null,1425,1425,1425,1425,1425,1425,1425,"N/A",1425,1425,1425,1425,1425,1425,1425]
[null,null,"Across Isolating Distance",null,"800 (+295)","800 (+295)","800 (+295)","800 (+295)","800 (+295)","800 (+295)","800 (+295)","N/A","800 (+295)","800 (+295)","800 (+295)","800 (+295)","800 (+295)","800 (+295)","800 (+295)"]
[3.1,"Rated Static Terminal Load\n(Longitudinal (Y) , Transverse (X), Vertical (Z))","Felixble Conductor","kN","(1.4, 0.9, -0.2)","(1.4, 0.9, -0.2)","(1.4, 0.9, -0.2)","(1.4, 0.9, -0.2)","(1.4, 0.9, -0.2)","(1.4, 0.9, -0.2)",null,null,"(1.4, 0.9, -0.2)","(1.4, 0.9, -0.2)","(1.4, 0.9, -0.2)","(1.4, 0.9, -0.2)","(1.4, 0.9, -0.2)","(1.4, 0.9, -0.2)"]
[null,null,"Rigid Busbar",null,"(0, 3.3, -1.3)","(0, 3.3, -1.3)","(0, 3.3, -1.3)","(0, 3.3, -1.3)","(0, 3.3, -1.3)","(0, 3.3, -1.3)",null,null,"(0, 3.3, -1.3)","(0, 3.3, -1.3)","(0, 3.3, -1.3)","(0, 3.3, -1.3)","(0, 3.3, -1.3)","(0, 3.3, -1.3)"]
[null,null,"Dropper",null,"(0, 1.8 , -0.3)","(0, 1.8 , -0.3)","(0, 1.8 , -0.3)","(0, 1.8 , -0.3)","(0, 1.8 , -0.3)","(0, 1.8 , -0.3)",null,null,"(0, 1.8 , -0.3)","(0, 1.8 , -0.3)","(0, 1.8 , -0.3)","(0, 1.8 , -0.3)","(0, 1.8 , -0.3)","(0, 1.8 , -0.3)"]
[]
[3.11,"Rated Dynamic Mechanical Terminal Load\n(Longitudinal (Y) , Transverse (X), Vertical (Z))","Felixble Conductor","kN","(0.5, 0.5, 0)","(0.5, 0.5, 0)","(0.5, 0.5, 0)","(0.5, 0.5, 0)","(0.5, 0.5, 0)","(0.5, 0.5, 0)",null,null,"(0.5, 0.5, 0)","(0.5, 0.5, 0)","(0.5, 0.5, 0)","(0.5, 0.5, 0)","(0.5, 0.5, 0)","(0.5, 0.5, 0)"]
[null,null,"Rigid Busbar",null,"(0, 2.6, 0)","(0, 2.6, 0)","(0, 2.6, 0)","(0, 2.6, 0)","(0, 2.6, 0)","(0, 2.6, 0)",null,null,"(0, 2.6, 0)","(0, 2.6, 0)","(0, 2.6, 0)","(0, 2.6, 0)","(0, 2.6, 0)","(0, 2.6, 0)"]
[null,null,"Dropper - Pinch",null,"(1.8, 0, 5. 5)","(1.8, 0, 5. 5)","(1.8, 0, 5. 5)","(1.8, 0, 5. 5)","(1.8, 0, 5. 5)","(1.8, 0, 5. 5)",null,null,"(1.8, 0, 5. 5)","(1.8, 0, 5. 5)","(1.8, 0, 5. 5)","(1.8, 0, 5. 5)","(1.8, 0, 5. 5)","(1.8, 0, 5. 5)"]
[null,null,"Dropper - Short circuit",null,"(3.2, 1.1, 5.1)","(3.2, 1.1, 5.1)","(3.2, 1.1, 5.1)","(3.2, 1.1, 5.1)","(3.2, 1.1, 5.1)","(3.2, 1.1, 5.1)",null,null,"(3.2, 1.1, 5.1)","(3.2, 1.1, 5.1)","(3.2, 1.1, 5.1)","(3.2, 1.1, 5.1)","(3.2, 1.1, 5.1)","(3.2, 1.1, 5.1)"]
[3.12,"Rated Bus Transfer current for disconnectors",null,"A","2400 (Vendor to Confirm)","2400 (Vendor to Confirm)","2400 (Vendor to Confirm)","2400 (Vendor to Confirm)","2400 (Vendor to Confirm)","2400 (Vendor to Confirm)",null,null,"2400 (Vendor to Confirm)","2400 (Vendor to Confirm)","2400 (Vendor to Confirm)","2400 (Vendor to Confirm)","2400 (Vendor to Confirm)","2400 (Vendor to Confirm)"]
[3.13,"Rated induced current switching class for earth switches (as specified in AS 62271-102)",null,null,"A","A","A","A","A","A","A",null,"A","A","A","A","A","A","A"]
[3.14,"Mechanical endurance class of disconnector (As specified in AS 62271-102)",null,null,"M1","M1","M1","M1","M1","M1",null,null,"M1","M1","M1","M1","M1","M1"]
[3.15,"Mechanical endurance class of Earth switches (As specified in AS 62271-102)",null,null,"M1","M1","M1","M1","M1","M1",null,null,"M1","M1","M1","M1","M1","M1"]
[3.16,"Electrical endurance class  of earth switch (As specified in AS 62271-102)",null,null,"E0","E0","E0","E0","E0","E0","E0",null,"E0","E0","E0","E0","E0","E0","E0"]
[4,"Charateristics of the Operating Mechanism and Associated Equipment"]
[4.0999999999999996,"Type",null,null,"Ganged,upright double break type motorized disconnector with one manual earth switch (R/H)","Ganged,upright double break type motorized disconnector with one manual earth switch (L/H)","Ganged,upright double break type motorized disconnector with two manual earth switches","Ganged,upright double break type motorized disconnector with one motorized earth switch (R/H)","Ganged,upright double break type motorized disconnector with one motorized earth switch (L/H)","Ganged,upright double break type motorized disconnector with two motorized earth switches ","Ganged, Stand alone motorized earth switch","Drive rod suitable for structures up to 6000mm","Ganged,upright double break type motorized disconnector with one manual earth switch (R/H)","Ganged,upright double break type motorized disconnector with one manual earth switch (L/H)","Ganged,upright double break type motorized disconnector with two manual earth switches","Ganged,upright double break type motorized disconnector with one motorized earth switch (R/H)","Ganged,upright double break type motorized disconnector with one motorized earth switch (L/H)","Ganged,upright double break type motorized disconnector with two motorized earth switches ","Ganged, Stand alone motorized earth switch"]
[4.2,"Length of the drive rod",null,"mm",6000,6000,6000,6000,6000,6000,6000,6000,6000,6000,6000,6000,6000,6000,6000]
[4.3,"Rated supply voltage for heater circuit",null,"Vac",240,240,240,240,240,240,240,null,240,240,240,240,240,240,240]
[4.4000000000000004,"Rated supply voltage for auxiliary circuits",null,"Vdc",110,110,110,110,110,110,110,null,110,110,110,110,110,110,110]
[4.5,"Rated supply voltage range for auxiliary circuits (a.c)",null,"Vac",null,null,null,null,null,null,null,null,"85%-110%","85%-110%","85%-110%","85%-110%","85%-110%","85%-110%","85%-110%"]
[4.5999999999999996,"Rated supply voltage range for auxiliary circuits (d.c.)",null,"Vdc","70%-110%","70%-110%","70%-110%","70%-110%","70%-110%","70%-110%","70%-110%"]
[4.7,"Degree of protection of enclosure",null,"IP",55,55,55,55,55,55,55,null,55,55,55,55,55,55,55]
[4.8,"Primary Terminal Palm Type (As specified in AS 62271-301)",null,null,"Table 1 (Figure 1 & 2)","Table 1 (Figure 1 & 2)","Table 1 (Figure 1 & 2)","Table 1 (Figure 1 & 2)","Table 1 (Figure 1 & 2)","Table 1 (Figure 1 & 2)",null,null,"Table 1 (Figure 1 & 2)","Table 1 (Figure 1 & 2)","Table 1 (Figure 1 & 2)","Table 1 (Figure 1 & 2)","Table 1 (Figure 1 & 2)","Table 1 (Figure 1 & 2)"]
[4.9000000000000004,"Phase Spacing",null,"mm",5800,5800,5800,5800,5800,5800,5800,null,5800,5800,5800,5800,5800,5800,5800]
[4.0999999999999996,"Phase-to-Earth Spacing",null,"mm",2900,2900,2900,2900,2900,2900,2900,null,2900,2900,2900,2900,2900,2900,2900]

{"sheet":"put in vendor schedule","index":2,"n_rows":9,"n_cols":14,"rows_kept":9,"cut":false,"hidden":true,"merged":[[5,0,6,0],[5,1,6,1],[5,2,6,2]]}
[]
[24,"Rated capacitor making (inrush) current","kAp",20,20,20,20,20,"back to back inrush",20,20,20,null,"As per AS62271.100 Table 5"]
[25,"Rated cable charging breaking current","A",25,25,31.5,50,25,"table 5 of std",25,31.5,50,null,"As per AS62271.100 Table 5"]
[26,"Rated out-of-phase breaking current","kArms",{"$f":"0.25*25","v":6.25},6.25,{"$f":"0.25*16","v":4},{"$f":"0.25*16","v":4},6.25,"AS62271.100 cl4.106 c)",null,null,null,null,"Out of phase is listed in table 24 of AS62271.100, but values are not the same as the ones listed here"]
[27,"Rated out-of-phase recovery voltage","kVrms",10.199999999999999,10.199999999999999,20.399999999999999,30.6,10.199999999999999,"AS62271.100 table 24",null,null,null,null,"Out of phase is listed in table 24 of AS62271.100, but values are not the same as the ones listed here"]
[28,"Rated transient recovery voltage","-","AS62271.100","AS62271.100","AS62271.100","AS62271.100","AS62271.100"]
[null,null,null,"Table 24","Table 24","Table 24","Table 24","Table 24"]
[]
[30,"First pole to clear factor","-",1.5,1.5,1.5,1.5,1.5,"in table 24",1.5,1.5,1.5,null,"As per AS62271.100 Table 5"]

{"sheet":"Technical Requirements1","index":3,"n_rows":84,"n_cols":8,"rows_kept":84,"cut":false,"hidden":true,"merged":[[65,0,66,0],[65,1,66,1],[65,7,66,7],[65,5,66,5],[65,6,66,6],[65,3,66,3],[65,4,66,4]]}
["1                                   ","SPECIFIC TECHNICAL REQUIREMENTS"]
["1.1                                ","COMMON EQUIPMENT RATINGS"]
[]
["Ref","Particulars","Units","12kV 25kA/3s Single Bus","12kV 25kA/3s Double Bus","24kV 16kA/3s Single bus","36kV 16kA/3s Single Bus","12kV 25kA/3s CBD Double Bus"]
[null,"System Conditions"]
[1,"Rated frequency","Hz",50,50,50,50,50]
[2,"Number of Phases",null,3,3,3,3,3]
[3,"Nominal Voltage","kV",11,11,22,33,11]
[4,"System Earthing",null,"Earthing Transformer","Earthing Transformer","Earthing Transformer","Earthing Transformer","Earthing Transformer"]
[5,"Switchboard Location",null,"Indoor","Indoor","Indoor","Indoor","Indoor"]
[null,"Common Ratings"]
[6,"Rated Voltage","kV",12,12,24,36,12]
[7,"Rated lightning impulse withstand voltage"]
[7.1,"to earth and between phases","kVp",75,75,125,170,75]
[7.2,"across the isolating distance","kVp",85,85,145,195,85]
[8,"Rated one minute power frequency withstand voltage"]
[8.1,"to earth and between phase","kVrms",28,28,50,70,28]
[8.1999999999999993,"across the isolating distance","kVrms",32,32,60,80,32]
[9,"Rated 3 second short-time withstand current","kA",25,25,16,16,25]
[10,"Rated peak withstand current","kAp",62.5,62.5,40,40,62.5]
[11,"Rated normal current"]
[11.1,"Busbar","A",2500,2500,1250,1250,2000]
[11.2,"Incomer circuits","A",2500,2500,1250,1250,2000]
[11.3,"Bus-section breaker","A",2500,2500,1250,1250,2000]
[11.4,"Feeder circuits","A",800,800,630,630,630]
[12,"Partial discharge level"]
[12.1,"each panel fully assembled with circuit breaker kVrms","pC","20 @7.6kV","20 @7.6kV","20 @15.2kV","20 @22.9kV","20 @7.6kV"]
[12.2,"fully assembled switchgear kVrms","pC","50 @7.6kV","50 @7.6kV","50 @15.2kV","50 @22.9kV","50 @7.6kV"]
[13,"Minimum dimension of copper earth bars","Mm","40 x 5","40 x 5","40 x 5","40 x 5","40 x 5"]
[14,"Degree of protection"]
[14.1,"External enclosure and between compartments","-","IP3X","IP3X","IP3X","IP3X","IP3X"]
[14.2,"Moving parts",null,"IP2X","IP2X","IP2X","IP2X","IP2X"]
[14.3,"Gas filled compartments, barriers between busbar and circuit breaker comaprtment",null,"IP65","IP65","IP65","IP65","IP65"]
[15,"Insulation level of auxiliary circuits and components"]
[15.1,"general","kVmin",2,2,2,2,2]
[15.2,"solid state electronic components 1.2 x 50 micro-sec 0.5J","kVmin",5,5,5,5,5]
[16,"Control voltages"]
[16.100000000000001,"trip and close circuits","Vdc",110,110,110,110,110]
[16.2,"spring charging circuit","Vac 1ph",240,240,240,240,240]
[16.3,"remote control and indication circuits ","Vdc",110,110,110,110,110]
[16.399999999999999,"cubicle heating circuits","Vac 1ph",240,240,240,240,240]
[null,"Circuit Breakers (as applicable)"]
[17,"Rated short circuit breaking current"]
[17.100000000000001,"a.c. component","kArms",25,25,16,16,25]
[17.2,"d.c. component (x/r ratio)","-",14,14,14,14,14]
[18,"Rated duration of short circuit","Sec",3,3,3,3,3]
[19,"Rated short circuit making current","kAp",62.5,62.5,40,40,62.5]
[20,"Rated back-to-back capacitor bank breaking current","Arms",400,400,400,400,400]
[21,"Rated operating sequence","-","O-0.3s-CO-15s-CO","O-0.3s-CO-15s-CO","O-0.3s-CO-15s-CO","O-0.3s-CO-15s-CO","O-0.3s-CO-15s-CO"]
[22,"Maximum break time","Sec",0.75,0.75,0.75,0.75,0.75]
[23,"Rating of auxiliary switches"]
[23.1,"continuous current rating","A",10,10,10,10,10]
[23.2,"break inductive circuit (time constant 40ms) at 110Vdc","A",2,2,2,2,2]
[24,"Operating tolerances of control voltage for guaranteed performance of equipment"]
[24.1,"for trip operation","%","70-120","70-120","70-120","70-120","70-120"]
[24.2,"for closing operation","%","85-120","85-120","85-120","85-120","85-120"]
[null,"Three position Disconnector"]
[25,"Disconnecting Mechanical Endurance ",null,null,null,null,null,"M1"]
[26,"Rated short time withstand current","kArms",25,25,16,16,25]
[27,"Rated duration of short circuit withstand","sec",3,3,3,3,3]
[null,"Motorised Disconnector"]
[29,"Disconnector motorised using an integral internal motor",null,"Yes","Yes","Yes","Yes","Yes"]
[30,"Continuous power rating of motorised Disconnector","W","≤100","≤100","≤100","≤100","≤100"]
[31,"Manual operation of the Disconnector possible in the event of an emergency",null,"Yes","Yes","Yes","Yes","Yes"]
[null,"Current Transformers* (as applicable)"]
[32,"Rated secondary withstand voltage","kV for",2,2,2,2,2]
[null,null,"1 min"]
[33,"Thermal limit secondary current","A",2,2,2,2,2]
[null,"Voltage Transformers* (as applicable)"]
[34,"Rated phase to phase primary voltage","kV",11,11,22,22,11]
[35,"Rated phase to phase secondary voltage","V",110,110,110,110,110]
[36,"Winding connections","-","YN/yn","YN/yn","YN/yn","YN/yn","YN/yn"]
[38,"Rated voltage factor and duration"]
[38.1,"voltage factor","-",1.9,1.9,1.9,1.9,1.9]
[38.200000000000003,"duration","sec",30,30,30,30,30]
[null,"Cable Box Requirements"]
[39,"Feeder Circuits"]
[39.1,"power cable size","-","400mm2","400mm2","400mm2","400mm2","630mm2"]
[39.200000000000003,"power cable type","-","1 core AL XLPE","1 core AL XLPE","1 core AL XLPE","1 core AL XLPE","1 core AL XLPE"]
[39.299999999999997,"power cable quantity","-","2 for each phase","2 for each phase","2 for each phase","2 for each phase","2 for each phase"]
[40,"Transformer and Bus-Section to Cable Circuits and Cable Connected Bus-Coupler (Double Bus Switchboard only)"]
[40.1,"power cable size","-","630mm2","630mm2","500 mm2","500 mm2","630mm2"]
[40.200000000000003,"power cable type","-","1 core CU XLPE","1 core CU XLPE","1 core CU XLPE","1 core CU XLPE","1 core CU XLPE"]
[40.299999999999997,"power cable quantity","-","3 for each phase","3 for each phase","  2 for each phase","  2 for each phase","3 for each phase"]